## Slide 1: PROFINET – An Introduction

## Slide 2
PROFINET Introduction

## Slide 3: What is PROFINET?
Ethernet open standard (IEC 61158) defined by PI (PROFIBUS and PROFINET International)
Fulfils Industrial Ethernet requirements
Uses TCP/IP and IT standards
Used for real time communication
Capabilities
Allows a smooth and easy integration of other legacy Field-buses
Simple distributed I/O and time-critical applications can be integrated into Ethernet communication
PROFINET is not PROFIBUS on Ethernet – It is much more!

## Slide 4: Why PROFINET?
PROFINET applies the Ethernet standard to automation. PROFINET enables high-speed (millisecond) and secure data exchange at all levels, and so makes it possible to implement innovative machine and plant concepts.
Flexibility and openness - PROFINET offers users maximum freedom in structuring their machine and plant architectures using Fiber optic and Wired/Wireless networks.
PROFINET‘s efficiency means optimal use of available user resources, and a significant increase in plant availability. Innovative Profinet products and the performance of PROFINET provide a sustained boost to company productivity.
Easy to implement since it is Ethernet based

## Slide 5: PROFIBUS and PROFINET Nodes
PROFIBUS Nodes PROFINET Nodes
PROFINET is catching up PROFIBUS DP at faster rate!

## Slide 6: PROFINET Myths and Facts
PROFIBUS runs at up to 12Mbit/s, whereas PROFINET runs at 100Mbit/s. Therefore PROFINET is about 8 times faster than PROFIBUS.
NOT TRUE!
  PROFINET gives very similar performance to PROFIBUS.
PROFINET will replace PROFIBUS in the next five years.
NOT TRUE!
  PROFINET will replace some PROFIBUS DP devices, but PROFIBUS PA will continue.
  Both DP and PA will be supported for many years to come.
PROFINET is not standard Ethernet
NOT TRUE!
  PROFINET always uses completely standard Ethernet. It just doesn’t always use TCP/IP protocols – only for not time critical communications.

## Slide 7: PROFINET Concepts
PROFINET IO
Used for modular distributed applications using Remote I/Os, Drives, HMIs, Smart MCCs
PROFINET CBA (Component Based Automation)
Used for Machine to Machine communication

## Slide 8: PROFINET Vs PROFIBUS

## Slide 9: PROFINET Components

## Slide 10: PROFINET Protocol Variations
PROFINET RT (Real Time)
RTA – RT Acyclic (Alarms, Configuration)
RTC – RT Cyclic (Data Communication)
PROFINET IRT (Isochronous Real time)
PROFINET NRT(Non Real Time)

## Slide 11: PROFINET Real-Time communication

## Slide 12: Real Time Protocols

## Slide 13: PROFINET RT Classes
RT Class-1 : Standard Communication, Used for Cyclic/acyclic data, no special switches are required
RT Class-2 : Real time Communication, Used for Cyclic data, special switches are required
RT Class-3 (IRT) : Isochronous Real time Communication, Used for Cyclic data in motion control applications , special switches and explicit communication planning are required

## Slide 14: PROFINET Redundancy Classes
Redundancy Class1 (MRP-Media Redundancy Protocol)
Ring redundancy for applications with typical switching times of 200 ms
Redundancy Class2 (MRP + MRRT-Media Redundancy Real Time)
Ring redundancy for RT requirements, switching times of a few ms
Redundancy Class3 (MRP +MRRT+ IRT Planning)
Ring redundancy for IRT requirements with bump-less switching

## Slide 15: PROFINET Conformance Classes

## Slide 16: PROFINET Communication Bandwidth

## Slide 17: PROFINET Bandwidth Reservation

## Slide 18: PROFINET –Real Time
When you try to use all layers..

## Slide 19: PROFINET Communication Bandwidth

## Slide 20: PROFINET Standard -Versions

## Slide 21: PROFINET ISO/OSI Model

## Slide 22: PROFINET ISO/OSI Model

## Slide 23: PROFINET Protocols

## Slide 24
PROFINET IO RT

## Slide 25: PROFINET IO RT Protocol
PROFINET IO is used for data exchange between I/O controllers (PLC, etc.) and I/O devices (field devices).
ROFINET IO uses the proven communication model and application view of PROFIBUS DP and extends it by Ethernet as the communication medium. Among other benefits, this provides a greater bandwidth and allows more stations on the network.
The PROFINET IO specifications define a protocol and an application interface for exchanging I/O data, alarms and diagnostics and for transmitting data records and logbook information. To exchange I/O data and alarms, PROFINET IO is based directly on the Ethernet protocol.
This real-time (RT) solution allows response times in the range of 5 ms, which corresponds to today‘s PROFIBUS DP applications.

## Slide 26: PROFINET IO RT Node Types
IO-Controller: This is typically the programmable logic controller (PLC) on which the automation program runs. This is comparable to a class 1 master in PROFIBUS. The IO-Controller provides output data to the configured IO-Devices in its role as provider and is the consumer of input data of IO-Devices (Ex: FCE PROFINET).
IO-Device: An IO-Device is a distributed I/O field device that is connected to one or more IO-Controllers via PROFINET IO. It is comparable to the function of a slave in PROFIBUS. The IO-Device is the provider of input data and the consumer of output data (Ex: PROFINET Drives).
IO-Supervisor: This can be a programming device, personal computer (PC), or human machine interface (HMI) device for commissioning or diagnostic purposes and corresponds to a class 2 master in PROFIBUS (Ex: Sycon.Net).

## Slide 27: PROFINET Topology

## Slide 28: PROFINET Protocols
RTA – Real Time Acyclic for Configuration, Alarms
RTC – Real Time Cyclic for Data
DCP – Discovery & Configuration Protocol for Device name assignment
LLDP – Link Layer Discovery Protocol for Topology identification
SNMP – Simple Network Management Protocol for Network diagnostics
MRP – Media Redundancy Protocol for Media Redundancy
PTCP - Precision Transparent Clock Protocol for Time Synchronization

## Slide 29: PROFINET Device Model
The PROFINET IO device model is comparable to PROFIBUS.
Compact field devices Modular field devices
(fixed degree of expansion) (variable degree of expansion)

## Slide 30: PROFINET Device Model
PROFIBUS IO modules and PROFINET bus interface (DAP*) IO device
I/O data are always assigned to sub-slots (real I/O channels).
Each sub-slot can contain I/O data or alarms.
I/O data are transferred with status information at the sub-slot level.
(DAP*) Device Access Point

## Slide 31: PROFINET Device Model
A Sub-slot is only allowed to be written by one Controller.

## Slide 32: Physical Device Management (PDev)
The PDev manages all the hardware relevant data within a device
In parallel to SNMP, all diagnostics and topology information can also be called up from the PDEV (Physical Device Object) using acyclic PROFINET services.

## Slide 33: PROFINET IO Device - Device Description
Description of Device properties are done using GSD files. It contains information about
Pluggable module type (AI 16 Channel etc)
Configuration data of the module
Configuration data of the channels (alarm limits, Input type etc)
Diagnostics information (wire break etc)
The GSD is XML based (called GSDML file)
Created and edited with standard XML editors (Ex. MS XML Notepad)
Structure of GSD Corresponds to the ISO 15745 Standard

## Slide 34: PROFINET APIs
API - Application Process Instance is an application inside PROFINET Device. Application Process Instance is addressed by APIx with default “0”. APIs>0 are reserved for Profiles.
A device may contain 1 or more APIs (Like ProfiDrive and ProfiSafe in a same device)

## Slide 35: PROFINET Application Relations (ARs)
Describes the relation between publisher and subscriber
There may be one or more ARs between a device and controller
Data exchange is possible only if ARs exist between device and controller
There may be several ARs in a device to several IO controllers.
Types of ARs:

## Slide 36: PROFINET Communication Relations
Communication Relations - CR: These specify the explicit communication channel between a consumer and a provider.
CRs within ARs are must for Data Exchange/Alarm notification.
Types of CRs:
* MCR – Multicast Communication Relation

## Slide 37: PROFINET Connections - Controller

## Slide 38: PROFINET Connections - Device

## Slide 39: Cyclic I/O data
Cyclic I/O data between IO Device and IO Controller are exchanged using RTC Protocol
Each IO data item has 2 attributes IOCS and IOPS (IO Provider Status and IO Consumer Status)
IOPS is transmitted simultaneously with the data and therefore it is consistent with data value
IOCS can only be returned from consumer to Provider only after reception of data and therefore it is inconsistent with data value.
IOCS and IOPS can have values GOOD and BAD

## Slide 40: Cyclic I/O data
Cyclic I/O data sequence:

## Slide 41: Cyclic I/O data

## Slide 42: PROFINET I/O Alarms
Process events are signaled within a PROFINET IO configuration by means of Alarms
IO device transmits alarms with Priority as “Real-Time” using RTA protocol
Both UP and DOWN alarms (Alarm/RTN) must be acknowledged by the IO controller
64 alarms can be transmitted in one Ethernet frame

## Slide 43: PROFINET I/O Alarm Types
Process alarms: Must be used if the message originates from the connected process, e.g., a limit temperature was exceeded. In this case, the IO-Device may still be operable. The data are not saved locally in the sub-module.
Diagnostic alarms: Must be used if the error or event occurs within an IO-Device (or in conjunction with the connected components, such as a wire break). Diagnostic and process alarms can be prioritized differently by the user. In contrast to process alarms, diagnostic alarms are identified as incoming or outgoing.

## Slide 44: PROFINET I/O Alarms
The overview figure shows the main structure of an alarm message or diagnostic entry used to signal an event. Any fatal error is always signaled as an alarm. Every alarm triggers an entry in the diagnostic buffer.

## Slide 45: PROFINET I/O Alarms
It is possible to send alarms as follows:
After an IO device was parameterized with Connect (Recovery)
When an event occurs in the field device
When an event occurs in the connected process

## Slide 46: PROFINET I/O Alarm Types

## Slide 47: PROFINET I/O Alarm Types contd…

## Slide 48: Alarm transmission sequence

## Slide 49: Acyclic data transmission
Non time-critical data are exchanged using acyclic data transmission
Takes place in NRT communication channel using Remote Procedural Calls (RPC) based on UDP/IP
Read/Write services are always consist of request and a subsequent response

## Slide 50: Name assignment with DCP

## Slide 51: Engineering & Data Exchange

## Slide 52: IP address assignment with DCP

## Slide 53: PROFINET Context Manager (CM)
Context management (CM):
Context manager manages the Application Relations (ARs) and Communication Relations (CRs) between IO controller and IO device
Initializes ARs and CRs
Setting relevant parameter for CRs Ex: timeouts and operating modes
Parameterization of Ethernet Device Driver (EDD)
Distribution of Parameters described in GSD
Implementation of Un-ambiguous identification of Data Exchange

## Slide 54: PROFINET Device Startup
Start MAC interface
Start LLDP (if supported)
Neighborhood information exchange
Start PDev
Station name and IP parameter assignment
Start Context Manager
Management of parameter and configuration data according to GSD file (check during startup, e.g., value range of analog modules) for an API.
Parameter monitoring for an AR
Establishment/clearance of an AR
Management of slots/sub-slots for I/O data

## Slide 55: PROFINET Device Startup

## Slide 56: Engineering & Data Exchange

## Slide 57: PROFINET IO Device Startup Classes
Applications that require short startup times therefore necessitate a transition from PROFINET IO to Interbus or PROFIBUS
As a result of the requirement, the startup is divided into three classes.
Normal StartUp (NSU)
Denotes the normal startup (7 seconds).
Accelerated StartUp (ASU)
Denotes a accelerated startup of the I/O devices within a time of less than 2 seconds (future startup procedure).
Fast StartUp (FSU)
Denotes a prioritized startup of selected I/O devices within a time less than 500 ms.

## Slide 58: PROFINET IO Startup Frames
Connect frame: Establishment of an AR and the configured CRs.
Write frame: Parameterizing of all configured submodules.
DControl frame: End detection of parameterization of the IO-Controller (also called ‘EndOfParameterization’).
CControl frame: End detection of parameterization of the IO-Device (also called ‘Application Ready’).

## Slide 59: PROFINET IO Frame Structure
Not all layers are needed

## Slide 60: PROFINET IO Frame Structure

## Slide 61: PROFINET IO Frame Structure
Prioritizing PROFINET RT Frames with VLAN-ID

## Slide 62: PROFINET IO Frame Structure
Connection Request Frame:
What is transferred?
RPC: Version(CLRPC), format, Object UUID, Interface UUID,…
NDR (Network Data Representation): length of data, error codes...
AR Block: Version, ARUUID, session key, CMI-Object UUID, CMInactivity-Timeout, length, station name
CR Input: version, IOCR-prop (RT_CLASS_), IOCR data length, send clock, red.ratio, phase, send offset,multicast Addr. (01-0E-CF-00-01-00), API, slot, subslot, offset in frame,....
CR Output: version, IOCR-prop, IOCR data length, send clock,red.ratio, phase, send offset,multicast Addr.(01-0E-CF-00-01-00 f orRT_CLASS_ 2 and 3), API, slot, su-bslot, offset in frame,....
Multicast CR: Provider or Consumer
Alarm: version, 0x8892, time-out, VLAN tag, ...

## Slide 63: PROFINET IO Frame Structure
Creating Data structure:

## Slide 64: PROFINET IO Frame Structure
Connection Request Frame:

## Slide 65: PROFINET IO Frame Structure
Transmitting Cyclical Data (Device -> Controller):

## Slide 66: PROFINET IO Frame Structure
Connection Response Frame

## Slide 67: PROFINET IO Frame Structure
Read Frame

## Slide 68: PROFINET IO Frame Structure
Write Frame

## Slide 69: PROFINET IO Frame Structure
End of Parameterization

## Slide 70: PROFINET IO Frame Structure
Ready Frame

## Slide 71: PROFINET IO Frame Structure
Alarm Frame

## Slide 72
PROFINET Features

## Slide 73: PROFINET Features
Simple Device Replacement

## Slide 74: PROFINET Features
Configuration-in-Run (CiR)
Uninterrupted plant operation including when reconfiguring devices and networks and when inserting, removing, or replacing devices or individual modules plays an important role in process automation .
All of these “Configuration in Run” measures (CiR) are carried out in PROFINET bumpless and without adversely affecting network communication. This ensures that plant repairs, modifications, or expansions can be performed without a plant shutdown in continuous production processes, as well.

## Slide 75: PROFINET Features
Device Discovery (Neighborhood Detection) via LLDP
Automation systems can be configured flexibly in a line, star, or tree structure. To compare the specified and actual topologies, i.e., to determine which field devices are connected to which switch port and to identify the respective port neighbor, LLDP according to IEEE 802.1 AB was applied in PROFINET IO.
PROFINET field devices exchange existing addressing information with connected neighbor devices via each switch port. The neighbor devices are thereby unambiguously identified and their physical location is determined (example in Figure 12: The delta device is connected to port 003 of switch 1 via port 001).

## Slide 76: PROFINET Features
Device Fast StartUp (FSU)
Fast Start Up (FSU) defines an optimized system power-up in which data exchange begins much faster starting with the second power-up since many parameters are already stored in the field devices. This optional path can be used in parallel to standard power-up (which is still used after a Power On and during the first power-up or reset). It must be possible to store communication parameters retentively for this.

## Slide 77: PROFINET Features
Device Fast StartUp (FSU) contd…

## Slide 78: PROFINET Features
Web Integration

## Slide 79: PROFINET Features
Tool Calling Interface (TCI)
Complex devices, such as drives, laser scanners, etc., often have their own engineering software and tools for making settings for these IODevices.
With the tool calling interface (TCI) these device tools can now be called directly from the plant engineering system for parameter assignment and diagnostics. In this case, the communication of PROFINET is used directly for the settings in the field device.
In addition to the directly integrated device tools, other technologies such as EDDL and FDT can also be used with appropriate adaption software.
TCI consists of the following
Main components:
Call interface: The user can call various field device user interfaces (Device Tools = DT) from the engineering system (ES). Functions are primarily initiated in the device tools through user interaction.
Communication interface: The TCI communication server allows the field device user interface (DT) to communicate with the field device.

## Slide 80: PROFINET Features
Tool Calling Interface (TCI) contd…

## Slide 81: PROFINET Features
Shared Device
Sharing is at sub-module level

## Slide 82: PROFINET Features
i-Device

## Slide 83: PROFINET Features
Shared + i-Device

## Slide 84: PROFINET Features
Network Management using SNMP

## Slide 85: PROFINET Features
Network Management using SNMP

## Slide 86: PROFINET Features
SNMP+LLDP – Network Management Software (Siemens SINEMA)

## Slide 87: PROFINET Features
SNMP+LLDP – T+H TH-Link and TH-Scope

## Slide 88: PROFINET Features
Extended Device Identification (Identification & Maintenance Functions)
Further information for standardized and simplified identification and maintenance is defined in additional I&M data records. I&M1-4 contain plant specific information, such as installation location and date, and are created during configuration and written to the device.

## Slide 89: PROFINET Features
Individual Parameter Server
The individual technology related parameters (e.g. the field definitions for a laser scanner) PROFINET IO device or module shall be saved in the PLC and restored at request.
With the function block FB24 "IPARSERV" individual technology related parameters ("iParameter") of any non-safety PROFINET IO device, or module can be saved on the PN IOController.

## Slide 90: PROFINET Features
MRP – Media Redundancy Protocol
Based on ring topology.
Max. number (50) of ring nodes of PN IO controller ,PN IO devices and Network infrastructure components (switches)
Configuration and Diagnostic in Engineering
Reconfiguration time 200ms
One MRP Master (Ex PLC) is mandatory in the ring, other devices can be MRP client

## Slide 91: PROFINET Features
Clock Synchronization using PTC-P
PTC-P – Precision Transparent Clock Protocol
Must for IRT mode operation
In large plants, the ability to assign alarms and status messages to a sequence of events is often required. For this purpose, an optional time stamping of these messages is possible in PROFINET IO.
In order to time stamp data and alarms, the relevant field devices must have the same time of day. To accomplish this, a master clock and the time synchronization protocol are used to set the clocks to the same time.

## Slide 92: PROFINET Features
PTC-P – Functional Principle:

## Slide 93: PROFINET Features
IRT Operation & Scheduling

## Slide 94
PROFINET Topologies

## Slide 95: PROFINET Topologies
Supported Topologies
Linear Bus (Line), Star, Ring, Tree

## Slide 96: PROFINET Topologies
Wireless Topology

## Slide 97
Fieldbus Integration

## Slide 98: PROFINET –Fieldbus Integration
Integrating Profibus DP/Profibus PA

## Slide 99: PROFINET –Fieldbus Integration
Integrating Profibus DP/Profibus PA using Hilscher Proxy
Single Profibus DP device using hilscher netLink NL 51N-DPL

## Slide 100: PROFINET –Fieldbus Integration
Integrating Profibus DP/Profibus PA using Hilscher Proxy
Multiple Profibus DP device using Hilscher netTap NT 100-RE-DP

## Slide 101: PROFINET –Fieldbus Integration
Integrating IO-Link

## Slide 102: PROFINET –Fieldbus Integration
Integrating AS-Interface using Proxy (SIEMENS IE/AS-I Link)

## Slide 103: PROFINET –Fieldbus Integration
Integrating Interbus using Phoenix contact Proxy FL NP PND- 4TX PB

## Slide 104: PROFINET –Fieldbus Integration
HART Over PROFINET:
Used mostly for Device Management
Devices can be wired (ET200M with HART Analog input) or Wireless(WirelessHART)

## Slide 105: PROFINET –Device Management
SIMATIC PDM – Devices connected to PROFINET

## Slide 106: PROFINET –Device Management
SIMATIC PDM – Devices connected to PROFIBUS DP

## Slide 107: PROFINET –Device Management
PROFINET and Device Management (Integrated):

## Slide 108: PROFINET –Fieldbus Integration
Other Fieldbus integration:
Integration with following Fieldbus/Protocols are also possible but they are more of gateway integration than integration via Proxy.
  Modbus RTU
  Modbus TCP
  DeviceNet
  CANOpen
  Foundation Fieldbus
  EtherNet/IP

## Slide 109
Profiles

## Slide 110: Profiles
Available Protocol Independent Application Profiles
PROFIsafe
PROFIdrive
PROFIenergy
Train profile for PROFINET
PA Profile for Process Automation

## Slide 111: Profiles
PROFIsafe:
Used for Safety controller-Safety I/O communication
Protocol Independent (Can be used on Profibus or Profinet)
Works based on Black-Channel Principle, Meets SIL3 requirements

## Slide 112: Profiles
PROFIsafe:
F-Host

## Slide 113: Profiles
PROFIdrive
The PROFIdrive profile describes the drive interface from the point of view of the control application, along with its mapping on the communication system.
It covers scenarios from simple frequency converters to highly dynamic servo drives

## Slide 114: Profiles
PROFIdrive application classes:
Category 1 – Standard drives (such as pumps, fans, stirring units, etc.)
Category 2 – Standard drives with technology functions
Category 3 – Positioning drives
Category 4 – Motion control drives with central, higher-level motion control intelligence and the patented "Dynamic Servo Control" position control concept
Category 5 – Motion control drives with central, higher-level motion control intelligence and position set point interface
Category 6 – Motion control drives with distributed motion control intelligence integrated in the drives

## Slide 115: Profiles
PROFIenergy:
No additional wiring required
Energy consuming Units (ECUs)(Ex. Motors) are switched off when it is not required and re-started just before when it is needed through coordinated switching

## Slide 116
PROFINET Diagnostics

## Slide 117: PROFINET Diagnostics
Network diagnostics using SNMP (already discussed)
Frame analysis using Wireshark
Frame analysis using NETLITIES

## Slide 118: PROFINET Diagnostics
Frame analysis using Wireshark
No special hardware required, port mirroring is sufficient
PROFINET Specific coloring rules(.ini files) can be imported and applied

## Slide 119: PROFINET Diagnostics
Wireshark Supported PROFINET Protocol and coloring rules:

## Slide 120: PROFINET Diagnostics
Frame analysis using PROCENTEC NETILITIES
Special hardware (PROFITAP) is required
Live List, SNMP diagnostics, topology detection, Wireshark analysis possible using NETILITIES software
ProfiTap helps capturing logs in wireshark without the need of port mirroring

## Slide 121: PROFINET Diagnostics
Live List:

## Slide 122: PROFINET Diagnostics
Live List:

## Slide 123: PROFINET Diagnostics
SNMP Diagnostics:

## Slide 124: PROFINET Diagnostics
Topology Detection:

## Slide 125
PROFINET Cabling System

## Slide 126: PROFINET Cabling System
Components:
PROFINET Switches
Industrial Ethernet cable
Ethernet connectors
IP connectors for outdoor
Fast Connect connectors
Cable Tester
Wireless System
Fiber optic Converter

## Slide 127: PROFINET Cabling System & Interconnection
Wireless System: R-Coax Cable
Useful for rotary equipments
1 section can be 80m long

## Slide 128: PROFINET Cabling System & Interconnection
Cable Tester

## Slide 129: PROFINET Cabling System & Interconnection
Fast Connect (FC) Technology:

## Slide 130: PROFINET Cabling System & Interconnection
Fast Connect (FC) RJ 45 plug:
M12 plug:

## Slide 131: PROFINET Cabling System & Interconnection
Industrial Ethernet FastConnect Cable 2 x 2
Industrial Ethernet FastConnect Cable 4 x 2

## Slide 132: PROFINET Cabling System & Interconnection
POF and PCF fiber-optic cables:

## Slide 133: PROFINET Cabling System & Interconnection
Industrial EtherNet switches and media converters

## Slide 134: PROFINET Cabling System & Interconnection
SCALANCE X-000 unmanaged switch:

## Slide 135: PROFINET Cabling System & Interconnection
SCALANCE X-100 Media Converters:
Single Mode & Multi mode fiber converters
Both LC and ST Type connectors possible

## Slide 136: PROFINET Cabling System & Interconnection
SCALANCE X-200 managed switch:

## Slide 137: PROFINET Cabling System & Interconnection
SCALANCE X-400 managed switch-Layer 3:

## Slide 138: PROFINET Cabling System & Interconnection
Wireless Communication:

## Slide 139: PROFINET Cabling System & Interconnection
Wireless Communication:

## Slide 140
PROFINET Device Simulators

## Slide 141: PROFINET Device Simulators
SIEMENS SIMBA PNIO
Can be used for virtual commissioning & Factory Acceptance Test (FAT)
Can be used for development and testing
Can be used for Product Demos
Can be used for Operator Training
2 Models available for 128/256 Devices
Both Data and Alarm simulation is possible

## Slide 142
Demos

## Slide 143: Demos
Sycon.Net for ProfiNet
Importing GSDML files
ProfiNet IO Engineering
Configuring Profibus DP, Interbus, AS-i Devices via Proxy
WireShark Analysis
DTMs for Profibus PA Devices
DTMs for HART Devices
ProfiNet Network Load Calculator Tool

## Slide 144: Books
Books:
Automating with PROFINET by Raimond Pigen and Mark Metter
Industrial communication with PROFINET by Manfred Popp

## Slide 145
Any Questions?